PMS610

INSTRUCTION BOOK

IB614101

Appendix B

MAINFRAME AND POWER SUPPLY

INSTRUCTIONS AND SCHEMATIC

Includes PMS610-24 and PMS610-48.

The PMS610 is a mainframe power supply for mounting FM SYSTEMS, INC. 600 series equipment. Up to three circuit board modules may be accommodated. These modules may be readily installed in the field with common hand tools; no soldering is required.

MECHANICAL:	Fits standard 19" wide rack. 1 3/4" High x 10 1/4" 			Deep.

CAPACITY:		Up to three FM SYSTEMS, INC. standard circuit 			board modules, each 5.3" wide x 9.35" deep, or one 			10.7" double-wide module and an additional single 			module.

INPUT POWER:	PMS610 105-125 VAC 60Hz at 0.4 Amps max. Standard 			5' 3-wire grounded U.S.A. cord set. PMS610-24 uses 			a 5 way binding post positive ground -24 VDC 0.5 			Amp max auto-reset fuse system. PMS610-48 uses a 5 			way binding post positive ground -48 VDC 0.5 Amp 			max Switching Power Supply with auto-reset fuse 			system.

OUTPUT POWER:	PMS610,PMS610-24,PMS610-48, output -24 VDC at 0.5 			Amps max distributed to the individual circuit 			cards with a daisy chain power wire internally.

CONNECTORS:	Accessible on the rear panel, provided as integral 			part of circuit board modules, see individual 			specification sheets for particulars.

WEIGHT:		PMS610=7 lbs. PMS610-24=6 lbs. PMS610-48=6 lbs.

MODULE CARD INSTALLATION

1.	Select which of the three positions will be occupied by the 	new circuit board module.

2.	Remove the mainframe from the rack, disconnect power.

3.	Remove the bottom cover, and the # 4-40 x 1/4" mounting 	studs adjacent to the new modules's location from the 	mainframe.

4.	Remove the appropriate rear-panel connector (blank) from the 	mainframe.

PMS610.ISB								PAGE 1 OF 4

Module card installation (continued).

5.	Remove the appropriate front-panel "nameplate" blank from 	the mainframe. To remove old nameplate carefully lift one 	corner, then slowly peel the nameplate from the aluminum 	panel. The old nameplate may be destroyed, but the aluminum 	panel should be essentially as new.

6.	Install the new circuit board module with the components 	toward top cover. Take care to avoid moving any of the 	preset controls (just a "slight" change can cause the unit 	to malfunction). Slip the connectors through the holes in 	the rear panel and drop the front edge of the circuit board 	onto the brackets attached to the front panel.

7.	Install two 3/8" lock washer and two 3/8" - 32 nuts on the 	outermost "F" connector barrels. Gently tighten the nuts 	while holding the circuit board to the mounting brackets.

8.	Install two #4-40 x 1/4" studs and lock washer to secure the 	front of the board to the mounting brackets.

9.	Remove the top cover from the mainframe.

10.	Connect the negative DC supply from the PMS610 power 	distribution daisy chain wire to the new circuit card.

11.	Push any L.E.D. (Light Emitting Diodes) straight into the 	appropriate mounting holes. Insert only until the dark 	collar around the colored L.E.D. is flush with the front 	panel, the collar must not protrude, in order to avoid 	interfering with the new nameplate.

12.	Mount the new front panel nameplate (Furnished with the 	circuit board module being installed). Temporarily set the 	new nameplate in place and check that all necessary cutouts 	are clear. Remove the paper peel coat from the adhesive 	backing of the nameplate, then slide the nameplate down 	around the L.E.D.'s onto the panel. Press gently to set the 	adhesive. Mount any additional panel components (Switches, 	meters, potentiometers etc.) with the hardware supplied. 	Gently tighten the fasteners to secure the components, do 	not over tighten.

13.	Mount the new rear panel connector identification strips as 	illustrated in the instruction book for the particular 	module being installed.

PMS610.ISB								PAGE 2 OF 4

Module card installation (continued).

14.	Connect input, output and power cables, The green "POWER-ON" 	indicator should be illuminated. Set any external controls 	as required.

CAUTION:

Most circuit board modules have several adjustments which are carefully factory set with precision instruments for optimum performance. Change only those which must be adjusted, some controls when mis-adjusted produce little change under normal operating conditions, but can seriously reduce the ability of the unit to function correctly under other conditions which may be encountered. Therefore, if you must adjust a control, place a mark on it before moving it, so that it may be returned to its original setting with reasonable accuracy.

15.	Disconnect power. Replace top and bottom covers and mount 	mainframe to rack. Reconnect power and check for normal 	operations of each module.

PMS610.ISB								PAGE 3 OF 4